SM SOLAR & ELECTRICAL

RESIDENTIAL SOLAR PV SITE ASSESSMENT

Field Capture Form + Sample Engineering Assessment Report

Purpose: Capture the information required to develop a safe, fit-for-purpose preliminary solar PV solution and a traceable detailed design. Complete the form on site; mark unknowns as “TBC” rather than guessing.

# PART A — FIELD SITE ASSESSMENT FORM

## A1. Visit and customer details

| Field | Capture on site |
| --- | --- |
| Assessment reference / version | ____________________________________________ |
| Date / time / assessor(s) | ____________________________________________ |
| Customer / contact / telephone | ____________________________________________ |
| Site address / estate / town / county | ____________________________________________ |
| GPS coordinates / altitude if available | ____________________________________________ |
| Property type / occupancy | ☐ Detached ☐ Apartment ☐ Maisonette ☐ Rental ☐ Other: __________ |
| Installation status | ☐ New installation ☐ Upgrade ☐ Fault investigation ☐ Expansion |
| Customer objective | ☐ Bill reduction ☐ Backup ☐ Off-grid ☐ Power quality ☐ Other: ______ |
| Preferred system | ☐ Grid-tied ☐ Hybrid ☐ Off-grid ☐ Needs advice |
| Budget range / target commissioning date | ____________________________________________ |
| Customer consent for photos / data | ☐ Yes ☐ No Notes: _____________________________ |

## A2. Existing electricity supply and bills

| Check / measurement | Record |
| --- | --- |
| Utility supply | ☐ KPLC ☐ Mini-grid ☐ Generator only ☐ None ☐ Other: ______ |
| Supply phase / nominal voltage | ☐ 1-phase ☐ 3-phase ☐ Unknown ¦ Measured: ______ V |
| Meter / account details (avoid unnecessary personal data) | Meter type: ______ ¦ Account reference (optional): ______ |
| Main service fuse / main breaker | Rating: ______ A ¦ Poles: ______ ¦ Condition: ______ |
| Main distribution board | Location: ______ ¦ Spare ways: ______ ¦ RCD/RCBO: ☐ Yes ☐ No ☐ TBC |
| Last 6–12 months of bills | Attach bills or record monthly kWh and KSh; note estimated vs actual readings. |
| Monthly consumption | Average: ______ kWh/month ¦ Highest: ______ ¦ Lowest: ______ |
| Monthly bill | Average: KSh ______ ¦ Tariff / TOU details if known: __________________ |
| Outages / voltage quality | Frequency/duration: ______ ¦ Measured min/max voltage: ______ |
| Generator / existing inverter / UPS | Make/model: ______ ¦ Rating: ______ ¦ Changeover/ATS: ______ |
| Earthing and bonding | Earth electrode / conductor / test result if measured: __________________ |
| Utility export permission / net-metering | Status: ☐ Not applicable ☐ Confirmed ☐ To verify with KPLC / current rules |

## A3. Load inventory and operating profile

List critical and non-critical loads separately. Record nameplate data or measured values where possible. Starting current, duty cycle and simultaneous operation are important; do not size from watts alone.

| Load / room | Qty | W or kW each | Hours/day | Days/week | Critical? | Start surge / notes |
| --- | --- | --- | --- | --- | --- | --- |
| Refrigerator / freezer | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |
| Lighting (LED) | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |
| TV / decoder / router | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |
| Laptop / office equipment | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |
| Water pump | __ | __ | __ | __ | ☐ Y ☐ N | Motor kW / starting method: ____ |
| Washing machine / iron / kettle | __ | __ | __ | __ | ☐ Y ☐ N | Heating loads may dominate demand |
| Microwave / oven / cooker | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |
| Air conditioner | __ | __ | __ | __ | ☐ Y ☐ N | Cooling capacity / input / surge: ____ |
| Other loads | __ | __ | __ | __ | ☐ Y ☐ N | ________________ |

| Load analysis | Record / outcome |
| --- | --- |
| Measured / estimated daily energy | ______ kWh/day; method: ☐ Bills ☐ Load schedule ☐ Meter/logger |
| Estimated coincident peak demand | ______ kW / kVA; basis and diversity assumptions: ______________ |
| Largest motor / compressor | Type: ______ ¦ Running: ______ W ¦ Starting: ______ / method: ______ |
| Critical-load circuits for backup | List circuits and estimated simultaneous load: _______________________ |
| Operating schedule | Day / night / weekend / seasonal changes: ________________________ |
| Future additions | EV, AC, pump, electric cooking, extension, etc.: __________________ |

## A4. Roof, ground mount and solar resource

| Check | Capture on site |
| --- | --- |
| Proposed array location | ☐ Roof ☐ Ground ☐ Carport ☐ Other: ______ ¦ Sketch/photo IDs: ______ |
| Roof material / form | ☐ Tile ☐ Iron sheet ☐ Concrete slab ☐ Other: ______ ¦ Pitch: ____° |
| Roof orientation / azimuth | Main usable planes: __________________ ¦ Compass/GPS method: ______ |
| Usable dimensions / area | Length: ____ m ¦ Width: ____ m ¦ Clear area: ____ m² |
| Roof condition / age / leaks | Condition: ______ ¦ Repairs required: ☐ Yes ☐ No ¦ Notes: ______ |
| Structure / load capacity | Rafters/purlins/spacing/material: ______ ¦ Engineer verification needed? ____ |
| Shading sources | Trees, tanks, parapets, neighbouring buildings, antennas: ____________ |
| Shading timing / tool | ☐ Morning ☐ Midday ☐ Afternoon ☐ Seasonal review ¦ Tool/photos: ______ |
| Access / fall protection | Safe ladder access, edge protection, anchor points, fragile areas: ______ |
| Mounting approach | ☐ Rail roof hooks ☐ Sheet-metal approved fixing ☐ Ballasted ☐ Ground frame ☐ TBC |
| Corrosion / coastal / harsh environment | Exposure: ______ ¦ Material/coating considerations: ________________ |
| Drainage / waterproofing / fire access | Water paths, penetrations, walkways, setbacks and emergency access: ____ |
| Solar resource / weather | Location for yield modelling; use appropriate irradiance source and losses: ____ |

## A5. Electrical installation and equipment locations

| Check | Capture on site |
| --- | --- |
| Proposed inverter location | Wall/room: ______ ¦ Indoor/outdoor: ______ ¦ Ambient ventilation: ______ |
| Battery location | Location: ______ ¦ Temperature/ventilation/security/clearances: ______ |
| DB / meter / utility point | Distances to inverter and battery: ______ m ¦ Photos / route sketch: ______ |
| Cable routes and lengths | PV DC: ____ m ¦ Battery DC: ____ m ¦ AC: ____ m ¦ Data/CT: ____ m |
| Cable containment / penetrations | Conduit/trunking/tray, UV/weather exposure, fire stopping: _____________ |
| Existing wiring condition | Conductor sizes, insulation, protection, overloaded circuits, exposed joints: ___ |
| Earthing / bonding / lightning | Earth arrangement, continuity, electrode test, bonding, external LPS/SPD coordination: ___ |
| Protection / isolation | PV DC isolator where required, string protection, DC/AC SPD, MCB/MCCB, RCD/RCBO, labels: ___ |
| Neutral-earth arrangement | Existing earthing system and inverter transfer/bonding requirements to be verified: ___ |
| Back-up changeover / grid interaction | Essential-load DB, interlocking, anti-islanding, export controls: __________ |
| Communications / monitoring | Wi-Fi/mobile signal, router, app ownership, data access: _________________ |
| Equipment service clearances | Manufacturer clearances and safe maintenance access: __________________ |

## A6. Safety, compliance and installation constraints

| Inspection item | Finding / action |
| --- | --- |
| Work at height / roof access | ☐ Acceptable ☐ Controls required ☐ Stop work ¦ Notes: __________ |
| Structural concerns / roof damage | ☐ None observed ☐ Further assessment required ¦ Notes: __________ |
| Electrical hazards / exposed live parts | ☐ None observed ☐ Isolate / electrician review ¦ Notes: __________ |
| Fire / battery placement / egress | ☐ Acceptable ☐ Review needed ¦ Notes: _____________________ |
| Water ingress / flooding / lightning exposure | Findings: __________________________________________ |
| Permits / approvals / utility coordination | Verify applicable current EPRA, KEBS, county, building and KPLC requirements for project type. |
| Customer expectations explained | ☐ Energy offset ☐ Backup limits ☐ Battery autonomy ☐ Maintenance ☐ Warranty |
| Photographs / attachments | ☐ Roof ☐ DB ☐ Meter ☐ Earth ☐ Cable routes ☐ Load nameplates ☐ Site overview |

## A7. Measurements, evidence and outstanding information

| Evidence item | Result / reference |
| --- | --- |
| Instrument used / calibration status | ____________________________________________ |
| Voltage / current / power measurements | ____________________________________________ |
| Earth resistance / continuity (if tested) | ____________________________________________ |
| Roof sketch / dimensions / orientation | ____________________________________________ |
| Bill / load schedule / single-line diagram | ____________________________________________ |
| Open questions / missing data | ____________________________________________ |
| Immediate hazards and mitigations | ____________________________________________ |

Assessor sign-off: __________________________ Date: __________    Customer / representative acknowledgement: __________________________ Date: __________

Acknowledgement confirms the site was visited and the observations recorded; it is not approval of final design, structural capacity or regulatory compliance.

# PART B — SAMPLE SITE ASSESSMENT REPORT

Illustrative case only — all site details and figures below are hypothetical.

## B1. Executive summary

Client: Sample household, Kisumu County. Objective: reduce KPLC energy purchases while maintaining selected essential circuits during outages. The site has a single-phase supply, a pitched iron-sheet roof with an apparently usable north-facing plane, and a separate wall location proposed for a hybrid inverter and lithium battery. A preliminary hybrid system is recommended for design development, subject to verification of bills, load inventory, roof fixing points, earthing, circuit segregation and manufacturer compatibility. This is not a construction-ready design.

| Item | Preliminary finding |
| --- | --- |
| System objective | Daytime energy offset + backup for selected essential loads |
| Supply | KPLC, single phase, assumed nominal 230 V; verify at site |
| Consumption | Assumed 420 kWh/month ≈ 14 kWh/day (validate against 6–12 months of bills) |
| Critical loads | Lights, refrigerator, TV/router, selected sockets; exclude cooker, kettle, iron and water heater unless separately assessed |
| Indicative architecture | Hybrid inverter + PV array + LiFePO₄ battery + essential-load circuits |
| Key hold points | Confirm roof structure and fixing method; actual load profile; earthing and protection; inverter surge capability; battery location; utility/export requirements |

## B2. Assumed site and load findings

| Parameter | Illustrative value | Design implication |
| --- | --- | --- |
| Average energy use | 14 kWh/day | Use actual bills and load schedule to refine energy target |
| Coincident peak demand | 2.5 kW estimated | Check inverter continuous rating and power factor |
| Largest motor | Refrigerator compressor; pump not yet confirmed | Check surge rating; capture pump nameplate if present |
| Roof | Iron sheet; north-facing plane; 20° assumed pitch | Confirm azimuth, purlin positions, corrosion and fixing details |
| Shading | Tree shading possible late afternoon | Carry out time/season shading review; avoid shaded strings where practical |
| Cable runs | PV 15 m; inverter-to-DB 8 m; battery 1.5 m assumed | Measure final routes and calculate voltage drop and current capacity |
| Battery location | Ventilated secure utility area | Confirm temperature, manufacturer clearances, fire and access considerations |
| Earthing | Existing earth electrode; no test result supplied | Test and document electrode/continuity; coordinate bonding and surge protection |

## B3. Preliminary sizing logic

The figures below demonstrate the calculation method, not a guaranteed energy yield. The final design must use the site's location-specific solar resource, orientation, shading, temperature, system losses and the customer's load timing.

| Design item | Illustrative calculation / selection | Qualification |
| --- | --- | --- |
| Daily energy target | 14 kWh/day total household use | Confirm with bills and load schedule; backup loads may be a smaller subset |
| PV array | Approx. 4.0 kWp (e.g., 7 × 580 W = 4.06 kWp) | Verify roof layout, module dimensions, MPPT voltage/current and string limits |
| Yield screening | At an assumed 4.5 peak-sun-hours/day and 0.75 performance ratio: 4.06 × 4.5 × 0.75 ≈ 13.7 kWh/day | Illustrative screening only; seasonal yield and actual losses may be materially different |
| Hybrid inverter | Indicative 5 kW, single-phase | Confirm continuous kW/kVA, overload duration, surge, MPPT windows, max PV power, DC current, grid code and essential-load output |
| Battery | Indicative 5.12 kWh nominal LiFePO₄ | At 80% usable energy, approx. 4.1 kWh usable before further losses; not enough to back up all 14 kWh/day |
| Backup duration | At 0.5 kW average critical load: 4.1 kWh ÷ 0.5 kW ≈ 8.2 h theoretical | Real duration lower after conversion losses, battery limits, temperature, ageing and variable load |
| PV strings | TBC after selecting exact module and inverter | Calculate cold-weather Voc, operating Vmp, MPPT current, parallel-string limits and DC protection |
| Cables / protection | TBC from final route, current, installation method and fault levels | Calculate ampacity, voltage drop, short-circuit withstand, disconnection and selectivity |

## B4. Proposed system concept

PV modules on an approved roof mounting system, with verified fixing into suitable structural members and weatherproofing.

PV DC cabling routed in UV-resistant, mechanically protected containment; DC isolators and string protection as required by the final topology and applicable standards.

Hybrid inverter installed in a dry, ventilated, accessible location in accordance with its manual.

Compatible lithium battery with BMS communications, correct DC fuse/breaker, cable sizing and manufacturer-required clearances.

Dedicated essential-load distribution board with clearly identified backed-up circuits; high-power heating and cooking loads excluded unless intentionally designed for.

AC protection, surge protection, earthing and bonding, neutral-earth switching/bonding, grid isolation and anti-islanding arranged to suit the selected inverter and local supply requirements.

Monitoring configured and handed over to the customer; labels, shutdown procedure, manuals and commissioning test results supplied.

## B5. Preliminary bill of materials (not a quotation)

| Item | Indicative quantity | Selection / verification note |
| --- | --- | --- |
| PV modules | 7 units, approx. 580 W each | Exact model, dimensions, warranty and electrical data to be confirmed |
| Hybrid inverter | 1 unit, approx. 5 kW, 1-phase | Select after peak/surge, backup and string checks |
| LiFePO₄ battery | 1 × approx. 5.12 kWh | Confirm inverter compatibility, current limits and expansion path |
| Roof mounting kit | 1 complete set | Quantity from measured roof layout and manufacturer's span/wind tables |
| PV DC cable and connectors | Measured length + design allowance | Correct PV cable rating; compatible connectors from same approved system |
| Battery cables and DC protection | 1 set | Size to maximum battery current and installation method |
| AC protection and changeover | As required by design | MCB/MCCB, RCD/RCBO where appropriate, isolators, SPD, essential-load DB |
| Earthing / bonding / labels | 1 complete set | Verify electrode, conductor sizing, bonding and local requirements |
| Conduit / trunking / glands / fixings | Measured quantities | Weatherproof, UV-resistant and mechanically suitable |
| Monitoring / commissioning | 1 set / service | Setup, functional tests, customer training and handover documentation |

## B6. Risks, actions and design hold points

| Priority | Issue / uncertainty | Required action before final design |
| --- | --- | --- |
| High | Actual monthly energy and critical-load profile not verified | Obtain 6–12 months of bills; complete load inventory and simultaneous-demand assessment |
| High | Roof structure and fixing capacity not confirmed | Inspect rafters/purlins and obtain structural review where capacity or condition is uncertain |
| High | Earthing, bonding and existing DB condition unknown | Inspection and appropriate electrical tests by competent personnel; record results |
| High | Exact inverter and module models not selected | Run manufacturer compatibility, string voltage/current, surge and battery checks |
| Medium | Late-day tree shading | Record shading at relevant times/seasons; adjust layout and model losses |
| Medium | Battery autonomy expectations not agreed | Agree backed-up circuits and target hours; explain usable energy and load shedding |
| Medium | Cable routes are estimated | Measure routes; complete voltage-drop, ampacity and protection coordination calculations |
| Medium | Utility export / approvals status unverified | Confirm current KPLC and applicable Kenyan regulatory requirements before grid-parallel commissioning |

## B7. Recommended design deliverables

Final load schedule showing daily energy, critical/non-critical loads, starting currents and coincident demand.

PV layout drawing with orientation, tilt, dimensions, access paths, shading notes and roof fixing details.

Single-line diagram covering PV DC, battery DC, inverter, AC DB, essential-load DB, grid connection, isolation, SPDs, earthing and changeover.

PV string calculation: cold-condition Voc, operating Vmp, MPPT window, current limits and module/inverter compatibility.

Cable schedule and calculations for current capacity, voltage drop, fault protection and installation method.

Battery autonomy calculation using usable capacity, efficiency, reserve/DoD, critical load and target backup hours.

Protection and earthing schedule, labels, shutdown instructions and commissioning checklist.

Priced BoQ, scope inclusions/exclusions, warranties, maintenance plan and customer acceptance.

## B8. Conclusion and recommendation

Proceed to detailed design for a hybrid system only after closing the high-priority hold points. The illustrative 4.06 kWp PV / 5 kW hybrid inverter / 5.12 kWh battery concept is a starting point for evaluation, not a final recommendation. If the main goal is bill reduction rather than backup, compare a grid-tied option; if the property requires prolonged autonomy or has no reliable grid supply, reassess PV and battery capacity against critical-load energy and worst-period solar availability.

| Prepared by | Reviewed / approved by | Customer acknowledgement |
| --- | --- | --- |
| Name: __________________ Signature: _______________ Date: ___________________ | Name: __________________ Signature: _______________ Date: ___________________ | Name: __________________ Signature: _______________ Date: ___________________ |

Important: This template is a field and preliminary design aid. It does not replace site-specific engineering, structural assessment, manufacturer instructions, electrical testing, or confirmation of current Kenyan laws, codes, utility requirements and permits.